## Sheet2
Version 14 - Feb 2026
Your Company Logo
Site Address or GPS Co-ordinates where available:
|  | User / Owners Contact Details | [6 empty] | Client's Name and Surname
E-mail address
Physical address
[9 empty] | Suburb | [9 empty] | Province | [8 empty] | Contact Number:
|  | Solar Contractors Details | [6 empty] | Installer Name and Surname
Accreditation number
Registration number with the Department of Labour
|  | Electrical Contractor's Details | [9 empty] | Same as above
Registered Person's Name and Surname
Accreditation number
Registration number with the Department of Labour where the contractor is registered as:
|  | Electrical Contractor is: | [8 empty] | Single Phase Tester | [5 empty] | Installation Electrician | [6 empty] | Master Electrician | [5 empty] | Working under General Control
Type of Installation
|  |  | Hybrid Inverter as Backup | [17 empty] | Hybrid Inverter with Solar PV
|  |  | Complete Section 1, 2 and 5 | [17 empty] | Complete Section 1, 2, 3, 4a + 4b(When Required) and Section5
SSEG Installation - Hybrid /Grid Tied Inverter used in Grid tied configuration without Storage
Complete Section 1, 3, 4 and 5
This document can only be issued at a site where there is an existing and valid Certificate of Compliance covering the Main electrical reticulation
For installations with more components please copy or duplicate the required sections
1 | Section 1a - Hybrid Inverter | [12 empty] | Number |  |  | 1 |  | of | [5 empty] | Brand Name:
2 | Inverter Serial Nr | [16 empty] | Inverter Capacity (in kW or kVA) | [10 empty] | kVA | [5 empty] | kW
3 | DB Board is |  |  |  | Single Phase |  |  |  |  | Three Phase |  |  |  |  | Inverter is wired | [5 empty] | To a single Phase | [5 empty] | To two Phases | [5 empty] | To all three Phases
4 | AC Mains Input to Inverter - Circuit Breaker Size | [17 empty] | Amps | [6 empty] | kA |  | Conductor Size | [8 empty] | mm2
5 | AC Output from Inverter to Load - Circuit breaker size | [17 empty] | Amps | [6 empty] | kA |  | Conductor Size | [8 empty] | mm2
6 | Earth Neutral Bridge | [7 empty] | Programmable / Internal relay | [9 empty] | External Contactor / Relay | [8 empty] | Hard Wired
7 | Inv. Casing bonded and continuous to Consumer Earth Bar 6.11 | [17 empty] | Ohm |  |  |  |  | Input CB Labelled | [7 empty] | Output CB Labelled
8 | Inverter Numbered with A Label (where there is more than 1) | [17 empty] | Yes | [8 empty] | Alternative Supply Label Fitted on Inverter
9 | Anti Islanding operation functional | [12 empty] | Tested |  |  |  |  | N/A - (To be used for installations where there is no available grid)
10 | Number of Built-in MPPT's | [12 empty] | Total Number of MPPT inputs
11 | MPPT Voltage Range | [5 empty] | Vmp | [7 empty] | Open Circuit Voltage Range | [7 empty] | Voc
1 | Section 1b - Hybrid Inverter | [12 empty] | Number |  |  | 2 |  | of | [5 empty] | Brand Name:
2 | Inverter Serial Nr | [16 empty] | Inverter Capacity (in kW or kVA) | [10 empty] | kVA | [5 empty] | kW
3 | DB Board is |  |  |  | Single Phase |  |  |  |  | Three Phase |  |  |  |  | Inverter is wired | [5 empty] | To a single Phase | [5 empty] | To two Phases | [5 empty] | To all three Phases
4 | AC Mains Input to Inverter - Circuit Breaker Size | [17 empty] | Amps | [6 empty] | kA |  | Conductor Size | [8 empty] | mm2
5 | AC Output from Inverter to Load - Circuit breaker size | [17 empty] | Amps | [6 empty] | kA |  | Conductor Size | [8 empty] | mm2
6 | Earth Neutral Bridge | [7 empty] | Programmable / Internal relay | [9 empty] | External Contactor / Relay | [8 empty] | Hard Wired
7 | Inv. Casing bonded and continuous to Consumer Earth Bar 6.11 | [17 empty] | Ohm |  |  |  |  | Input CB Labelled | [7 empty] | Output CB Labelled
8 | Inverter Numbered with A Label (where there is more than 1) | [17 empty] | Yes | [8 empty] | Alternative Supply Label Fitted on Inverter
9 | Anti Islanding operation functional | [12 empty] | Tested |  |  |  |  | N/A - (To be used for installations where there is no available grid)
10 | Number of Built-in MPPT's | [12 empty] | Total Number of MPPT inputs
11 | MPPT Voltage Range | [5 empty] | Voc | [12 empty] | Vmp
12 | Signatures for this page | [17 empty] | Dated:
13 | [6 empty] | Installer | [11 empty] | Registered person
14 | Section 2 - Batteries | [8 empty] | Lead-Acid |  |  |  |  | Lithium |  |  |  |  | Other please specify
15 | Battery Brand/Name | [16 empty] | All Batteries are the same brand and size | [11 empty] | Yes |  |  |  | No
16 | Charge rate as set per inverter | [10 empty] | Amps (NRS097 charge limit) | [8 empty] | Battery Serial Nr
17 | Voltage Type | [5 empty] | Battery Installation Type
18 |  | Low Voltage (48V-96V) | [6 empty] | Rack / Server Type | [7 empty] | Nr of Racks or Cabinets or Stacks | [13 empty] | R / C / S
19 |  | High Voltage (>100V) | [6 empty] | Wall Hung | [7 empty] | Nr of batteries (or nr per Cabinets / Stacks / Rack)
20 | [8 empty] | Floor Standing | [7 empty] | Batteries in cabinets / Racks / Stacks are wired in | [12 empty] | Series |  |  | Parallel
[9 empty] | Stacked | [7 empty] | Total Capacity per Cabinet / Stack | [7 empty] | ± | [8 empty] | kWh
21 | Total Installation Capacity | [8 empty] | kWh
22 | Jumpers are enclosed and is not accessible in order to be measured. | [16 empty] | YES |  |  | N/A
| Battery Enclosure Bonded to Consumer Earth Bar | [13 empty] | Ohm |  | Battery Cabinet Bonded to Consumer Earth Bar | [14 empty] | Ohm
23 | Take-off Lead from battery to Busbar / Fuse | [13 empty] | mm2 |  | Jumpers in between parallel batteries - Interlinks | [14 empty] | mm2
Cable Sizing to be - each mm2 = 1kA Fault current 6.7.3.2
24 | [7 empty] | Fuse/s | [17 empty] | Rack / Server / Cabinet
25 |  |  |  | Amp |  |  |  | Circuit Breaker/s |  |  |  |  | is/are connected between the inverter and | [12 empty] | Busbar
26 |  | This is for external Fuse Protection (not the fuse or Circuit Breaker built into the battery) | [23 empty] | Battery
27 | [7 empty] | Fuse/s | [17 empty] | Rack / Server / Cabinet
28 |  |  |  | Amp |  |  |  | Circuit Breaker/s |  |  |  |  | is/are connected between the busbar and | [12 empty] | Busbar
29 |  | This is for external Fuse Protection (not the fuse or Circuit Breaker built into the battery) | [23 empty] | Battery
30 | Section 3 - Solar Modules
31 | Number of modules | [7 empty] | Total PV System Size | [7 empty] | kW |  | Module Size | [5 empty] | Watt |  |  | Module Brand
Where possible, test and record the following values (alternatively calculate values), values indicated could be for single strings or parallel strings
[6 empty] | String 1 |  | String 2 |  | String 3 |  | String 4 |  | String 5 |  | String 6 |  | String 7 |  | String 8
32 | Nr. Of Modules |  |  | Qty
33 |  |  |  | Voc | [19 empty] | Nameplate Rating | [5 empty] | Calc. |  |  |  | Tested / Read
34 |  |  |  | Vmp | [19 empty] | Nameplate Rating | [5 empty] | Calc. |  |  |  | Tested / Read
35 |  |  |  | Imp | [19 empty] | Nameplate Rating | [5 empty] | Calc.
36 |  |  |  | Isc | [19 empty] | Nameplate Rating | [5 empty] | Calc.
37 | Single String
38 | Parallel String | [33 empty] | Inverter
39 | PV Modules Bonded and continuous to Consumer Earth Bar | [15 empty] | Ohm. |  | Values for row 33 and 34 were measured at which point? | [15 empty] | Combiner
40 | All MC4 Type couplers are of the same Brand | [11 empty] | Yes |  |  |  |  | Unknown | [16 empty] | At the String
41 | Mounting Structure Type | [11 empty] | Rooftop |  |  |  |  | Ground Mount | [6 empty] | Carport | [5 empty] | Other
42 | Module Frames are supported by Mounting Structure Rail made of | [16 empty] | Aluminium | [6 empty] | Galvanised | [5 empty] | Other
43 | Mid and End Clamps are made of | [11 empty] | Stainless Steel |  |  |  |  | Aluminium | [6 empty] | Galvanised | [5 empty] | Other
44 | Conductors passing under tiles / through roofing materials are protected from Mechanical damage | [29 empty] | Yes |  |  |  |  | N/A
45 | Bolts on Mid and End Clamps are Torqued to which Value | [15 empty] | Nm |  | Modules/Strings are numbered and labelled | [11 empty] | Yes |  |  |  |  | N/A
46 | Positive and negative cables enter the roof/building at the same place (Meaning Conductors are bundled together) | [29 empty] | Yes |  |  |  |  | N/A
47 | Labelling of DC strings where they enter/ exit a wall/ roof (712.514.102 - Live parts marking) | [29 empty] | Yes |  |  |  |  | N/A
48 | Wiring loops were minimised according to 712.521.103 | [23 empty] | Unknown | [5 empty] | Yes |  |  |  |  | N/A
49 | Signatures for this page | [8 empty] | Dated:
50 | Installer | [8 empty] | Registered person
51 | Section 4a - Combiner / Fuse Box / Gateway | [12 empty] | Fuse Box |  |  |  | Combiner Box |  |  |  |  | Gateway or Other please specify
The Installation parameters for the Gateway / Fuse / Combiner box does not fall into the fields listed in this Test Report
52 | Short Circuit Protection | [10 empty] | DC Circuit breaker | [5 empty] | DC Fuse |  |  |  |  | Fuse / Circuit breaker Size | [8 empty] | Amps |  | and |  |  | kA
Either Fuse or Circuit breaker Protection can be used on the positive conductors
53 | Reverse Current Protection | [6 empty] | DC Circuit breaker (non-polarised; that can detect reverse current) | [15 empty] | DC Fuse |  |  | DC Fuse Size |  |  |  |  | Amps |  | and |  |  | kA
Not all Circuit breakers can protect against DC reverse current. For Fuses, there will be fuses on the negative and positive conductors
54 | Isolation | [10 empty] | DC Circuit Breaker | [5 empty] | DC Rated Isolator |  |  |  |  | Isolation device Size | [8 empty] | Amps |  | and |  |  | kA
(Fuse may not be used as an isolation device) - Double Pole
55 | Location |  |  |  | Combiner Boxes are Installed at floor level and can be reached without a step ladder
56 | Labels |  |  |  | String Conductors are numbered and Labelled | [11 empty] | Combiner / Fuse Box is labelled "Danger - Live DC Conductors - Solar Power"
57 | Section 4b - External MPPT | [10 empty] | ALL MPPT casings are bonded and continuous to earth
58 | (Pos) Short Circuit Protection | [10 empty] | DC Circuit breaker | [5 empty] | Fuse or Circuit breaker Size | [6 empty] | DC Fuse | [6 empty] | Amps |  | and |  |  | kA
Either Fuse or Circuit breaker Protection can be used on the positive conductors
59 | (Neg) Reverse Current Protection | [16 empty] | DC Fuse | [6 empty] | DC Fuse Size | [6 empty] | Amps |  | and |  |  | kA
Only Fuses can be used. Circuit breakers do not protect against reverse current, Fuses will be situated on the negative conductors
60 | Isolation | [10 empty] | DC Disconnect | [5 empty] | DC Rated Isolator | [6 empty] | Isolation device Size | [6 empty] | Amps |  | and |  |  | kA
(Fuse may not be used as an isolation device and cannot be opened under load) - Double Pole
61 |  |  |  |  | String Conductors are numbered and Labelled | [14 empty] | MPPT's are numbered
62 |  |  |  |  | MPPT's are labelled with a "Danger - Live DC Conductors - Solar Power" Sign
63 | Section 5 - General
64 | Earth Leakage has been fitted after inverter | [18 empty] | Yes |  |  | N/A |  |  |  |  | Earth Neutral Bond before RCD
65 | DC Surge Protection fitted | [10 empty] | Type 1 and 2 combined | [7 empty] | Yes |  |  | N/A |  | Type 2 |  |  | Yes |  | Type 3 |  |  | Yes |  |  | N/A
66 | AC Surge Protection has been fitted | [10 empty] | Type 1 and 2 combined | [7 empty] | Yes |  |  | N/A |  | Type 2 |  |  | Yes |  | Type 3 |  |  | Yes |  |  | N/A
67 | Metal Wireways and trunking Bonded and continuous to Consumer Earth Bar | [18 empty] | Yes |  |  | N/A
68 | Earth Loop impedance test before E/L on DB Powered by Inverter | [20 empty] | Ω | Neutral Loop test at point of control | [11 empty] | Ω
69 | Plug Test has been completed and Earth Leakage Units are fully operational | [18 empty] | Yes |  |  | N/A
70 | Resistance of earth continuity conductor | [20 empty] | Ω
71 | Prospective Short circuit current at point of control for the DB Board where inverter is installed | [25 empty] | kA
72 | Elevated voltage between incoming neutral and external earth | [24 empty] | V
73 | Voltage at Main DB with no load for each phase to neutral | [17 empty] | Red |  |  | V | White |  |  | V | Blue |  |  | V
74 | Voltage at Main DB with load for each phase to neutral | [17 empty] | Red |  |  | V | White |  |  | V | Blue |  |  | V
75 | Lightning risk assesment completed | [18 empty] | Yes |  |  |  |  | N/A
76 | SLD single line diagram attached next to DB | [18 empty] | Yes |  |  |  |  | Available as soft copy
77 | Audible or visual warning where DB's are split | [18 empty] | Audible |  |  |  |  | Visual
78 | Sections Completed under this test report
79 |  | 1 |  | Yes |  | N/A
80 |  | 2 |  | Yes |  | N/A
81 |  | 3 |  | Yes |  | N/A
82 |  | 4a |  | Yes |  | N/A
83 |  | 4b |  | Yes |  | N/A
84 |  | 5 |  | Yes |  | N/A
85 | Signatures for this Document and Test Report | [15 empty] | Dated:
86 | Installer | [15 empty] | Registered person
Note on F166: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Where batteries are fully charged during the test, the current might actually be zero. Therefore, calculating this value is preferred